BILCO Type ACDSV smoke vents are designed to guard against noise intrusion while providing the security of automatic smoke venting. Vents feature STC 50 and OITC 46 sound ratings along with ISO 140-18 Rainfall Sound Rating – 37.5 db.  They are ideal for concert halls, theaters and other interior applications that require limited noise from the outside. Vents are available in steel construction and in a number of UL-Listed standard and special sizes. For more information, please visit our website www.bilco.com or call 1-800-366-6530.

SECTION 077236

AUTOMATIC SMOKE VENTS

(BILCO TYPE ACDSV)

GENERAL

SUMMARY

Work Included:  Provide factory-fabricated double-leaf automatic smoke vents.

SUBMITTALS

Product Data:  Submit manufacturer’s product data.

Shop Drawings:  Submit shop drawings including profiles, accessories, location, fusible links, adjacent construction interface, and dimensions.

Warranty:  Submit executed copy of manufacturer’s standard warranty.

QUALITY ASSURANCE

Manufacturer:  A minimum of 5 years experience manufacturing similar products.

Installer:  A minimum of 2 years experience installing similar products.

Manufacturer’s Quality System: Registered to ISO 9001 Quality Standards including in-house engineering for product design activities.

DELIVERY, STORAGE AND HANDLING

Deliver products in manufacturer’s original packaging.  Store materials in a dry, protected, well-vented area. Inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

WARRANTY

Manufacturer’s Warranty:  Provide manufacturer’s standard warranty.  Materials shall be free of defects in material and workmanship for a period of five years from the date of purchase. Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge.

PRODUCTS

MANUFACTURER

Basis-of-Design Manufacturer: Type ACDSV Double-Leaf Automatic Roof Fire Vent by The BILCO Company, P.O. Box 1203, New Haven, CT 06505, 1-800-366-6530, Fax: 1-203-535-1582, Web: www.bilco.com.

AUTOMATIC ROOF FIRE VENT

Furnish and install where indicated on plans: metal fire vent Type ACDSV, size [insert: width (______) x length (______)]. Length denotes hinge side. The roof fire vent shall be double leaf. The roof fire vent shall be preassembled from the manufacturer.

Performance characteristics:

Vent(s) shall be UL listed.

Covers shall be reinforced to support a minimum live load of 40 psf (195 kg/m2) with a maximum deflection of 1/150th of the span or 90 psf (439 kg/m2) wind uplift.

Corrosion resistant gas springs shall open the vent covers simultaneously when latch is manually released or when heat breaks the UL listed fusible link. Opening shall be in a controlled manner to avoid damage to surrounding roof surfaces.

Entire roof fire vent shall be weathertight with fully welded corner joints on cover and curb.

Latch mechanisms shall hold the covers in the closed position without overstressing the fusible link and withstand 90 psf (439 kg/m2) wind uplift forces acting on the cover.

Latch operation: When heat parts the UL listed fusible link, the latch shall release instantaneously, allowing vent covers to open. The latch shall be designed for easy resetting, after a fire or test, so that the covers cannot be latched closed unless the mechanism has been reset properly. Manufacturer shall provide instructions for resetting the latch with each unit.

Sound Transmission Rating: Vent(s) shall carry STC-50 and OITC 46 sound ratings.

ISO 140-18 Rainfall Sound Rating – 37.5 db.

Covers: Shall be 14-gauge (1.9mm) paint bond G-90 galvanized steel with a 5-3/4” (146mm) beaded flange with formed reinforcing members.

Gasket: Dual EPDM gaskets shall be permanently adhered to the underside of the covers.

Cover insulation: Shall be mineral wool of 4" (102mm) in thickness, fully covered and protected by a 12-gauge (2.75mm) paint bond G-90 galvanized steel liner.

Curb: Shall be 12" (305mm) in height and of 10-gauge (3.5mm) paint bond G-90 galvanized steel with a fixed center channel. Curb shall be formed with a 6-7/8” (175mm) flange with 7/16" (11mm) holes provided for securing to roof deck. Curb shall be equipped with integral metal capflashing of 14-gauge (1.9mm) paint bond G-90 galvanized steel and feature the Bil-Clip® flashing system, including stamped tabs, 6" (153mm) on center, to be bent inward to hold single-ply roofing membrane securely in place.

Curb insulation: Shall be 4" (102mm) mineral wool insulation, fully enclosed by a 10-gauge (3.5mm) paint bond G-90 galvanized steel liner.

Lifting mechanisms: Corrosion resistant gas springs open covers automatically against a 10 lb/ft2 (49Kg/m2) snow/wind load. Gas springs shall have built in dampers to assure a controlled rate of opening and automatically lock the covers in the full open position. A release mechanism shall be provided to allow the covers to be closed.

Latch mechanism: Shall be the BILCO Thermolatch® II positive hold/release mechanism with a separate latching point for each cover controlled by a single UL listed 165°F (74°C) fusible link. Fusible link shall be curb mounted on a non-hinged end to allow the latching mechanism to be easily reset from the roof level.

Hardware: Corrosion resistant gas springs and hot dip galvanized steel stop cables. All other hardware is zinc plated/chromate sealed.

Finish: Factory finish shall be alkyd base red oxide primer.

EXECUTION

EXAMINATION

Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.  Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work.

Test units for proper function and adjust until proper operation is achieved.

Test fusible link and install replacement fusible link after testing.

Repair finishes damaged during installation.

Restore finishes so no evidence remains of corrective work.

ADJUSTING AND CLEANING

Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION